Description:

Centrifugal roof fan with backward curved impeller and vertical discharge. Housing made of weather-resistant aluminium AlMg3. The air outlet is protected by a protection grille against intrusion, birds, dirt and other foreign objects. Baseplate of galvanized steel sheet with deep drawn air inlet and preassembled screws for the possibility of connecting pipe flanges and accessories according to DIN 24154 / EN 12 220. The fan has been conceived for easy mounting on roof socket (optional accessory) without the necessity of removing the housing. Swing-out fan unit for cleaning and maintenance purposes. Suited for use according to VDI 2052. The incorporated grease pan and drain avoid roof soiling and ensure a controlled drainage of fat impregnated impurities.

The backward curved strong impeller is mounted on the shaft of an energy saving internal rotor EC motor. The impeller is dynamically balanced according to the quality class G 6.3 of DIN / ISO 1940, on 2 planes. Via the integrated EC controller it is possible to continuously adjust the speed of the motor using a 0-10 V signal. The motor is located outside the air stream and as such optimally protected against soiling. The motor protection is provided by integrated thermal monitoring of the motor electronic.

CE marking according to EC Declaration of Conformity for Electromagnetic Compatibility EMC - Directive 2004/108/EC. EC - Declaration of Incorporation according to the Machinery Directive 2006/42/EC - Directive 2009/125/EC (Reg.

1253/2014/EU).

Technical data:

Volumetric flow (V): m³/h Pressure increase (Δp fa): Pa Efficiency static max. (η fa): 57,8 % Efficiency total max. (ηt): 59,0 %

Rated voltage (U): 230, 1~ V Rated frequency (f): 50 Hz Rated power consumption (P N): 1418 W Current consumption max. (I max.): 10,1 A Rated speed (n): 2550 min-1

Protection class motor: IP 54

Protection class terminal box: IP - Ambient temperature max. (t A): 50 °C Medium temperature max. (tM): 120 °C

Inlet sound power level (L WA5): 82 dB(A) Outlet sound power level (LWA6): 86 dB(A)

Dimensions housing (L x W x H): 742x742x604 mm

Weight: 48,1 kg

Wiring diagram: 147362

Manufacturer:

ruck Ventilatoren GmbH Max-Planck-Str. 5

97944 Boxberg

Tel. 07930-9211300 [www.ruck.eu](http://www.ruck.eu/)

|  |  |  |
| --- | --- | --- |
| Available accessories:  DSF 355-10 | 126160 | Roof socket, flat roof size 355 |
| DSF 355-12 up to 19 |  | Sloped roof socket, size 355, slope optional in 3° increments (3-24°) |
| DSS 355-10 | 126403 | Roof socket, flat roof, sound insulated, size 355 |
| DSS 355-12 up to 19 |  | Sloped roof sound insulated socket, size 355, |
|  |  | slope optional in 3° increments (3-24°) |
| DAP 355 | 133963 | Roof adapter plate size 355 |
| DVK 400 10 | 152897 | Roof - Gravity shutter size 400 |
| DAS 400 F4 | 150093 | Roof - Inlet spigot size 400 |
| DAF 400 | 109826 | Roof - Inlet flange size 400 |
| MTP 20 | 128146 | Potentiometer 0-10V, stepless |
| MTP 30 | 143289 | Stepped potentiometer, +10Vdc, step 1+2 adjustable, step 3 100% Vdc |
| MTP 40 | 147359 | Potentiometer for connection in terminal box, sales unit 20 pcs. |
| CON P1000 | 115259 | Constant pressure control with day-night switch function |
| CLIMASET 01 | 111314 | Accessories set for CON P1000, pressure hose, nipples and screws |
| SEN P1000 | 126080 | Differential pressure sensor |
| SEN AIR | 148641 | Airflow and temperature transducer |